## Bid ACE
ACE Item | Scope | Risk? | AES SME | Point Person | Internal Note | Response to EPC | ACE Item 2025.08.08 Change Log
7. 750 kcmil cable length mentioned in the client's 30% design is 164,678 LNFT less than PRE's calculated value( three phase). Our analysis is that the client has not considered, the parallel run lengths in the calculation. | AC Electrical Systems | Yes | Development Engineer | Sam Desai | What quantity did PRE price? This would be a ~50% increase to cable qty/cost | if this is in referecne to DC cable, the westwood 30% shows one way length in the 30% design. | Removed in 8/08: this discrepancy note does not appear.
1. Base bid proposal pricing (based on 30%) includes cost for 1,080 silt fence rock outlets although the Westwood 30% drawings do not show these. Primoris assumed silt fence rock outlets would be used at intervals of 250 feet along silt fence. | Civil Works | TBD | Development Engineer | Sam Desai |  |  | Removed in 8/08: not present.
2. Base bid proposal pricing (based on 30%) does not include cost for fiber roll, rock check dams, or diversion swales since the Westwood 30% drawings do not show these. | Civil Works | Yes | Development Engineer | Sam Desai | What additional erosion control scope above and beyond 30% drawings can we reasonably expect? Suggest we push PRE to include what they see as necessary. |  | Removed in 8/08: not present.
1. Piles are assumed to be non coated (black steel) ranging from W6X12 up to W6X25, with tracker pile reveal height ranging from 5.25’ to 6’, with a max embedment depth of 9’. | Procurement | TBD | Development Engineer | Sam Desai | AES assumed 3 mil galv, Eng to determine whether black steel is viable. |  | Max embedment 8' changed from 9', based on “Nextracker’s FT HailPro 60° stow” loads.
1. Pricing for MET equipment includes design engineering, procurement, installation, and commissioning of the following equipment: 13 Zenith MET Stations: -1 GHI Pyranometer, 1 POA Pyranometer, 3 RPOA Pyranometers, 1 All-in-one Weather Sensor, 1 Rain Gauge, 1 Lightning Rod*, 4 Surge Arrestors* (1 per array pyranometer) 13 Eclipse Soiling Stations 5 Standalone Albedometers: -1 GHI Pyranometer, 1 RGHI Pyranometer *Lightning rod and surge arrestors added at recommendation of MET vendor due to the project being located in an area of elevated lightning risk. | Plant Controls and Communications | TBD | SCADA Engineer | Sam Desai |  |  | Changed: counts reduced in 8/08 to 10 Zenith MET, 10 Eclipse soiling, 3 standalone albedometers.
2. Ampacity values provided by the client's Ampacity report was used. | AC Electrical Systems | No |  | 0 |  |  | Changed: ampacity based on geotech thermal resistivity; trefoil configuration; spiderplow installation; 90% compaction.
Assumption - A5 - Ampacity values provided by the client's Ampacity report was used. | Detailed Design & Construction Engineering - 30% to IFC | No |  | 0 |  |  | Changed: ampacity based on geotech thermal resistivity; trefoil configuration; spiderplow installation; 90% compaction.
2. SCADA proposal includes the latest exhibits for Crescent PV, which is different from BF2. Based on ask from AES to make suggestions for improvements we have come up with some items and possible approximate cost savings: -Canary Historian ~$500K -Cisco Firewalls ~ $20K -1GB Field Network ~ $200K. | Plant Controls and Communications | No |  | 0 |  |  | Changed: 8/08 VE deltas reduced — Canary Historian ≈$400k and 1 GB Field Network ≈$150k (Cisco Firewalls ≈$20k unchanged).
3. Price excludes module washing during or after installation. | Solar PV Field Mechanical | Yes | Execution PM | Jon Coyne | Need to include mod washing. | Need to include mod washing. | Changed: 8/08 adds a below-the-line one-time mobilization & wash option
Assumption - A12 - Primoris has assumed that the on-site water wells can be used for the dust mitigation purpose. Throughout the project duration, Primoris would require ~100 million gallons of water for backfill and dust control. Proposal assumes that the water can be purchased through the landowner at $0.50 per barrel of water. One barrel of water shall be defined as 37 gallons. We have assumed that there is at least one well in East and one in West parcel within the project boundary and each well produces ~100k gallons per day. | Civil Works | Yes | Developer | Page Bolin | Need to compare against landowner agreement to determine whether this cost assumption is adequate. Is water supply adequate to 100M gallon need? | Need to compare against landowner agreement to determine whether this cost assumption is adequate. Is water supply adequate to 100M gallon need? | Changed: ~80 million gallons in 8/08 (price and 37-gal barrel definition unchanged).
2. An alternate price for procurement, installation and commissiong of 153 SMA model SC4400 UP-US Inverters is offerred. To meet the project schedule an accelerated Commissioning Schedule (50 calendar day duration) and a supply of commissionng spares is recommended. | Procurement | No |  | 0 |  |  | alternate now 116 SMA SC4400 UP-US with 40-day accelerated commissioning (was 153 units, 50 days).
Base price includes 90% pre-drill. Adder for 100% pre-drill will be provded below the line. | Solar PV Field Mechanical | No |  | 0 |  |  | 8/08 base includes 93% pre-drill in 8/08 (adder for 100% remains).
5. Pricing for basins aligns with Westwood's 30% drawings which indicate all basins will be temporary converted to permanent. Price may change for basin reclamation if basins are to be temporary only. | Civil Works | TBD | Development Engineer | Sam Desai |  |  | 8/08 assumes all basins will be temporary; price may change if permanent basins are required.
1. Assume average module delivery rate of 30MW/week. | Procurement | Yes | Execution PM | Jon Coyne | Workable rate of delivery per ExPM | Please propose range and max velocity. AES will evaluate with Vendor. | 18 MW/week
1. Power factor of 0.94 assumed for losses calculations | AC Electrical Systems | TBD | Development Engineer | Sam Desai |  |  | 1. Power factor of 0.92 assumed for losses calculations
Exclusion - E1 - PPS has not included any rock drilling in this proposal. | AC Electrical Systems | Yes | HV Engineer | Tyler Hock | What is our internal assumption on transmission structure rock drilling? | What is our internal assumption on transmission structure rock drilling?
1. Assume there are no un-surveyed underground lines not included in the client-provided surveys. | Civil Works | No | Development Engineer | Sam Desai | AES has done a lot of due dilligence, fair for them to exclude.
3. The proposal does not include any allowance for rock, slurry, or cased/shored excavation. We are assuming dry, stable earth excavation for completion of all excavation activities pending being provided a geotechnical report. | Civil Works | Yes | Development Engineer | Sam Desai | Do we need to consider rock in basin excavation?
Not responsible for crop damage, livestock protection or drain tile repair/mitigation. | Civil Works | Yes | Development Engineer | Sam Desai | Is there any indication of drain tile presence onsite? | No drain tiles in irrigated portion, no crops in the field. May leave livestock as a risk.
Includes 6' chain link fence with 1' 3 barbed wires and gates. | Civil Works | TBD | Development Engineer | Sam Desai | Are there any requirements on fencing in site control agreement? Alternately, do we want them to price ag fence.
2. Provisions for discovery and/or removal of underground tanks, flow lines, pipes, and foundations are not included. | Civil Works | TBD | Development Engineer | Sam Desai | Any demo scope of already identified underground infrastructure?
4. Excludes removal of underground tanks, flow lines, pipes, and foundations. | Civil Works | TBD | Development Engineer | Sam Desai
Native soil will be suitable for backfilling trenches. No costs have been included for imported or engineered backfill. | DC Electrical Systems | No | Development Engineer | Sam Desai
Price includes rough-in, grounding, and inverter installation. Lightning protection for PV Inverters is excluded. | AC Electrical Systems | TBD | Development Engineer | Sam Desai
3. MV Rev C cables with concentric neutral size 18#14 AWG is assumed for 500kcmil, 750kcmil and 1000kcmil cables and CN size of 17#14 AWG for 4/0 cables. These sizes are bigger than the size mentioned in the client's 30% design. | AC Electrical Systems | TBD | Development Engineer | Sam Desai
5. MVAC cable collection loss % assumed is 0.85. | AC Electrical Systems | TBD | Development Engineer | Sam Desai
3. Back of module temperature sensors, as AES has informed PRE that neither the ISO or forthcoming PPAs shall require them. | Plant Controls and Communications | TBD | Development Engineer | Sam Desai
Assumption - A3 - Piles are assumed to be non coated (black steel) ranging from W6X12 up to W6X25, with tracker pile reveal height ranging from 5.25’ to 6’, with a max embedment depth of 9’. The pile sizes are based on Nextracker's HailPro 60 degree stow top of pile loads. | Detailed Design & Construction Engineering - 30% to IFC | TBD | Development Engineer | Sam Desai
Assumption - A4 - Power factor of 0.94 assumed for losses calculations. | Detailed Design & Construction Engineering - 30% to IFC | TBD | Development Engineer | Sam Desai
Assumption - A6 - MV Rev C cables with concentric neutral size 18#14 AWG is assumed for 500kcmil, 750kcmil and 1000kcmil cables and CN size of 17#14 AWG for 4/0 cables. These sizes are bigger than the size mentioned in the client's 30% design. | Detailed Design & Construction Engineering - 30% to IFC | TBD | Development Engineer | Sam Desai
Assumption - A8 - Assumed T-line losses=0 for calculations. | Detailed Design & Construction Engineering - 30% to IFC | TBD | Development Engineer | Sam Desai
Assumption - A9 - MVAC cable collection loss % assumed is 0.85. | Detailed Design & Construction Engineering - 30% to IFC | TBD | Development Engineer | Sam Desai
Assumption - A14 - Native soil will be suitable for backfilling trenches. No costs have been included for imported or engineered backfill. | Civil Works | TBD | Development Engineer | Sam Desai
Assumption - A16 - The proposal does not include any allowance for rock, slurry, or cased/shored excavation. We are assuming dry, stable earth excavation for completion of all excavation activities pending being provided a geotechnical report. | Civil Works | TBD | Development Engineer | Sam Desai
Bid has been prepared based on PRE’s experience in Texas and assumes the following: (1) any executed contract will be considered separated for Texas sales/use tax purposes and (2) AES will provide an executed Texas exemption certificate, Form 01-339. Sales tax has been included on all items consumed/used by the contractor, i.e. construction equipment, consumables, etc. Additionally, bid includes estimated sales tax due on tracker and piles. PRE will coordinate with AES to confirm any exemptions to be claimed, ensure Schedule of Values is separated for Texas sales/use tax purposes, and calculate estimated taxes due. Changes to SOV format and/or exemptions to be claimed may result in a change in Contract Price. | Contractor General | No | Developer | Page Bolin | So long as we are including estimates of taxes due, regardless of exemption in the future
1. Our schedule assume immprove of the joint Solar/oil well Access Roads can begin as soon as the RUA is approved (i.e. since the roads are already in place, a driveway permit will not be required) | Civil Works | No | Developer | Page Bolin | Please confirm this with Ben. Ben is point on RUA.
2. Our schedule assumes the Wilbarger County Road Use Agreement (RUA) will be approved by Oct 1, 2025. | Civil Works | No | Developer | Page Bolin | Please confirm this with Ben. Ben is point on RUA.
3. Assume there will be no interference with Wind construction activites on the Access Roads included in the RUA. | Civil Works | Yes | Developer | Page Bolin | Wind gen-tie will enter the solar area of construction north of FM1763 - which is an access road to the west solar area. In addition, the wind and solar gen tie's will be parallel and adjacent to each other north of FM 1763 going through a solar parcel and up to the SY/SB | The wind gen-tie will enter the solar construction area north of FM1763 (which is also the access road to the west solar area), and wind and solar gen-ties will run parallel/adjacent through a solar parcel up to the SY/SB. Please revise your bid to address potential access and schedule conflicts in this area, including any required coordination measures or cost impacts.
6. Assume all powerlines, roads, and easements can be bored under. | AC Electrical Systems | No | Developer | Page Bolin | Within Reason. We are not aware of any local regulation prohibiting boring.
Assumption - A2 - Bid has been prepared based on PRE’s experience in Texas and assumes the following: (1) any executed contract will be considered separated for Texas sales/use tax purposes and (2) AES will provide an executed Texas exemption certificate, Form 01-339. Sales tax has been included on all items consumed/used by the contractor, i.e. construction equipment, consumables, etc. Additionally, bid includes estimated sales tax due on tracker and piles. PRE will coordinate with AES to confirm any exemptions to be claimed, ensure Schedule of Values is separated for Texas sales/use tax purposes, and calculate estimated taxes due. Changes to SOV format and/or exemptions to be claimed may result in a change in Contract Price. | Contractor General | No | Developer | Page Bolin | So long as we are including estimates of taxes due, regardless of exemption in the future
Assumption - A13 - FM1763, CR 105S, and FM 2897S Roads are suitable for construction traffic and may be used for site access. Refer to the provided draft "Site Access Routes" for full breakdown of assumed lengths and maintenance plan. Price to be finalized with RUMA final approval. Primoris has also assumed there will be no other construction traffic on these roads during our construction schedule. | Civil Works | Yes | Developer | Page Bolin | These are public county roads that will likely require additional upgrades or enhancements to adequately handle sustained heavy construction traffic. Please refer to approved RUMA for potential requirements. Since these roads are public county roads, it would be presumptive to assume that there will be no other construction traffic using these roads during the term of construction. There are several other projects being developed in the area, as well as two in-service wind farms, that may require construction work during the development of the solar project. Those projects may require the use of these roads for access. | These are public county roads that may require upgrades or enhancements per the final RUMA, and they are likely to be used by other construction projects and existing wind farms during our construction period. Please revise your bid to account for potential road improvements and shared traffic conditions.
1. Performance testing: Primoris agrees to an ASTM standard-based Capacity Test, which is the industry standard performance guarantee in the US. This is the same approach taken on Bellefield II. All performance testing shall be executed at the plant level, not at the circuit level. | Contractor Testing & Commissioning | No | Execution Engineer | Naveena Kodakandla | We want plant level testing
2. Contractor guarantees that the Capacity Test output will be equal to or greater than 97% of the Expected Capacity in accordance with certain criteria as will be more precisely detailed in an exhibit to the EPC Contract (the “Guaranteed Capacity”), the terms of which shall be subject to negotiation by the parties prior to the execution of the EPC Contract. | Contractor Testing & Commissioning | Yes | Execution Engineer | Naveena Kodakandla | AES to determine allowable guaranteed capacity | AES to determine allowable guaranteed capacity
2. The Crescent Archeological Study ("8._Crescent-Historical_-_Archaeological_Study-Final_04-22-2023.pdf") identifies two potential historical structures within the project area. However, it is unknown if the structures are extant and an aerial imagery search does not identify any visible structures. Therefore, Primoris has assumed these structures are no longer extant and do not require avoidance. | Civil Works | No | Permitting | Megan Lisburg | Confirm what scope needs to be included re historical structures. ML Update: We are following an Unanticipated Discovieries Plan for historic resources. Will be created internally and shared with EPC prior to mobilization. Preliminary procedures are included in EPC RFP Exhibit C4.
3. Assume the project lies outside of the tricolored bat range and that there are no tree clearing restrictions due to bats. | Civil Works | No | Permitting | Megan Lisburg | Project is outside of bat range
4. Assume tree clearing, chipping and spreading can start anytime. Assume the SWPPP need to be inplace prior to stump removal. | Civil Works | No | Permitting | Megan Lisburg | Project is outside of bat range.
Texas Kangaroo Rat is not expected to occur in the project area. Primoris assumes no survey, mitigation and/or avoidance is required for this species. | Civil Works | No | Permitting | Megan Lisburg | Project has been fully surveyed for TKR; they are confirmed absent. No further work needed. EPC to follow EPC RFP Exhibit C4 recommendations for avoidance if TKR are discovered onsite.
2. Assume all soil spoils will be spread on-site. | Civil Works | No | Permitting | Megan Lisburg | ML and CZ: This is fine, but we will need to ensure that this is managed in the EPC's EMP, Exhibits D-1.2, Exhibit C-4, and Exhibit B-1. EPC to follow VSMP-recommended soil spoil management practices. If not properly managed, we risk compaction and/or erosion concerns. VSMP will be amended to include BMPs for soil spoils. Please let us know if the Exhibits get redlined and they remove the requirement to do soil testing after grading (Exbibit B-1) or the requirement to follow our VSMP (Exhibit C-4). | This is to be managed by the EPC to prevent compaction and erosion concerns.
Assumption - A15 - All soil spoils will be spread on-site. | Civil Works | No | Real Estate | Josh Phillips
Assumption - A1 - PPS assumes ROW can be used as laydown area. | AC Electrical Systems | Yes | Real Estate | Josh Phillips | ROW type matters (public county, utility, or private leased corridors). Laydown areas are typically within LOD and on private land. Environmental compliance, lease terms, and permitting could all limit or prohibit ROW laydown. We already have designated laydown in the Westwood 30% design. | Please identify the specific ROW(s) you are referring to (e.g., public county roads, utility easements, or private leased corridors). Use of ROW for laydown is subject to lease terms, environmental and permitting restrictions, and AES approval, and may not be permissible. Laydown should be limited to areas designated in the approved Westwood 30% design unless otherwise directed by AES. Revise your bid accordingly to reflect permitted laydown areas only.
2. Primoris is requesting 0.4% of total modules for construction spares. | Procurement | Yes | Execution PM | Jon Coyne | Internal assumption is 5 spares per MW -0.27% - look into Longi historicals
3. Per the exhibit D-8 and D-8.1, Primoris will provide a dedicate on-site staff to develop the social management plan, community engagement meetings, create risk mitigation (includes noise, dust, signage), job fair planning and participation, weekly/ monthly compliance updates, and owner-led social impact session. The cost associated with this will be provided as below the line allowance. | Contractor General | Yes | Execution PM | Jon Coyne | Work with Execution PM to determine how much scope we want to include
4. Scanning of each barcode on every module installed is excluded. | Solar PV Field Mechanical | Yes | Execution PM | Jon Coyne | Check against B-1 req, also check with Tax to determine if required | Check against B-1 req, also check with Tax to determine if required
5. Double handling of modules is not included. | Solar PV Field Mechanical | Yes | Execution PM | Jon Coyne |  | Confirm that double-handling as a result of contractor activities or schedule delay is included.
2. Price excludes Hail protection of the PV modules when in the pallet or installed on the tracker (60 degree HailPro). | Solar PV Field Mechanical | Yes | Contract Manager | Daniela Rojas | I suggest to ask them to price it. However, it'll be our SME the one ultimately making the technical decision, and, based on the quoted price, Execution will make the final determination. This should be assiged to the Eng. Team first. | Please provide a price add for hail protection of the PV modules when in the pallet and when installed on the tracker (60° HailPro). Final determination on inclusion will be made by the Engineering and Execution teams based on your quoted price.
The tracker design is using 60 degree stow which differs from the 30% Westwood design 75 degree. Domestic Content: 19.3 pts | Procurement | Yes | Estimator | Brent Anderson |  | This is lower DC product from Nextracker, need to align on pricing for intended product.
1. SMA 4400 (153 units) to be supplied by AES. | Procurement | No |  | 0
3. The SMA Inverters offerred here include a 55 degree C ambient temperature option. | Procurement | No |  | 0
2. Uncoated “black steel” foundation design will be included in the proposal. | Procurement | No |  | 0
1. Pre-drill PLT's was not performed by ANS and pre-drill with an undersize hole will be required to confirm the driven pile design parameters. | Detailed Design & Construction Engineering - 30% to IFC | No |  | 0
2. Additional PLT drivability testing will be required to confirm areas of pre-drill for driven pile install. | Detailed Design & Construction Engineering - 30% to IFC | No |  | 0
3. Includes additional PLTs and supplemental Geotech studies. | Detailed Design & Construction Engineering - 30% to IFC | No |  | 0
4. An additional corrosion study will be provided by JDH corrosion, based on the corrosion potential in the geotech report. | Detailed Design & Construction Engineering - 30% to IFC | No |  | 0
1. Price includes Engineering services for Electrical, Civil, and Structural through IFC. | Detailed Design & Construction Engineering - 30% to IFC | No |  | 0
2. Max design temperature at the site used is 42.1C according to ASHRAE. | Detailed Design & Construction Engineering - 30% to IFC | No |  | 0
3. SCAN station used to obtain soil temperature and moisture value - 2202 Vernon | Detailed Design & Construction Engineering - 30% to IFC | No |  | 0
1. Construction spares have been included for the PV plant construction. | Contractor General | No |  | 0
2. Per the exhibit P, no O&M spares are included. The Parties shall enter into a Change Order to amend the Contract Price to include such elected Spare Parts post Notice to Proceed. | Contractor General | No |  | 0
1. Primoris has included 520,000 cubic yards of cut and 520,000 cubic yards of fill has been carried per the table on PV-C.02.01. Primoris has assumed that all material will be cut to fill on site and each parcel will be balanced. | Civil Works | No |  | 0
4. All dirt work is full machine excavation. | Civil Works | No |  | 0
3. Proposal pricing include cost for third party SWPPP inspections. | Civil Works | No |  | 0
4. The project schedule dictates we start construction work on the East side of the project and the west side at the same time. Consequently we will not be following the SWPPP staging plan described in the 30 design, drawing PV-C.01.05r1. | Civil Works | No |  | 0
2. We have included installation and maintenance of the Switchyard/Substation Access Road in our scope. Depending on the construction schedule for the switchyard,the road may be built before our schedule dictates (Mar'26) |  | No |  | 0
1. FM1763, CR 105S, and FM 2897S Roads are suitable for construction traffic and may be used for site access.Refer to the provided draft "Site Access Routes" for full breakdown of assumed legths and maintanance plan. Price to be finalized with RUMA final approval. Primoris has also assumed there will be no other construction traffic on these roads during our construction schedule. | Civil Works | No |  | 0
1. Removal and disposal of existing and/or non-project generated refuse or debris beyond what's described in the 30% design. | Civil Works | No |  | 0
3. Excludes temporary or permanent relocation of existing utilities beyond what's described in the 30% design. | Civil Works | No |  | 0
Includes O&M building for 725MWdc size project per the O&M Specs 'O&M_Portable_Facility_Parameters' provided by AES. | Civil Works | No |  | 0
Tracker row lengths are based on module dimensions from the provided module data sheet Hi-Mo 545W (2278 x 1134 x 30 mm). | Solar PV Field Mechanical | No |  | 0
1. Modules considered are LR5-78HBD-545M (Hi-Mo 545W). Modules will be procured and delivered to site by Owner. Primoris will be responsible for offloading, Staging, and Installation of modules. | Solar PV Field Mechanical | No |  | 0
Price includes Shoals DC Collection System. Installation of PV string wiring is included in 'Furnish & Install PV Wire Harnessing & Combiner Box Disconnects' bid item. | DC Electrical Systems | No |  | 0
Includes purchase & install of Harness, Trunk Bus, LBDs, Splice Boxes. | DC Electrical Systems | No |  | 0
Includes purchase and imstall of cable management system. | DC Electrical Systems | No |  | 0
4. Ground cable size assumed in the design is 7#7AWG which is equivalent to the client mentioned 1/0 Cu. | AC Electrical Systems | No |  | 0
1. Pricing is based on client provided 30% design drawings. | AC Electrical Systems | No |  | 0
2. Assumed MVOH losses=0 for calculations. | AC Electrical Systems | No |  | 0
3. 30% MV OH design does not include part numbers or material quantities so estimated quantities were used to determine pricing. | AC Electrical Systems | No |  | 0
4. We have assumed a total of 330,500lbs for the steel poles. | AC Electrical Systems | No |  | 0
5. We have assumed a total of 1,015CY of concrete for the drilled piers. | AC Electrical Systems | No |  | 0
Assumption - A1 - Tariffs are not included in the base price SOV. The estimated tariffs through mid-July, 2025 have been presented below the line for each procurement category. | Contractor General | No |  | 0
Assumption - A7 - Ground cable size assumed in the design is 7#7AWG which is equivalent to the client mentioned 1/0 Cu. | Detailed Design & Construction Engineering - 30% to IFC | No |  | 0
Assumption - A10 - Max design temperature at the site used is 42.1C according to ASHRAE. | Detailed Design & Construction Engineering - 30% to IFC | No |  | 0
Assumption - A11 - SCAN station used to obtain soil temperature and moisture value - 2202 Vernon. | Detailed Design & Construction Engineering - 30% to IFC | No |  | 0
Assumption - A19 - Assume there are no un-surveyed underground lines not included in the client-provided surveys. | Civil Works |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Assumption - A20 - The Crescent Archeological Study ("8._Crescent-Historical_-_Archaeological_Study-Final_04-22- 2023.pdf") identifies two potential historical structures within the project area. However, it is unknown if the structures are extant and an aerial imagery search does not identify any visible structures. Therefore, Primoris has assumed these structures are no longer extant and do not require avoidance. | Civil Works |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Assumption - A21 - Assume the project lies outside of the tricolored bat range and that there are no tree clearing restrictions due to bats. | Civil Works |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Assumption - A22 - Texas Kangaroo Rat is not expected to occur in the project area. Primoris assumes no survey, mitigation and/or avoidance is required for this species. | Civil Works |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Assumption - A23 - Exhibit Q (Interconnect Agreement) does not specify the In-Service date. Our schedule assumes power will be available for Substation testing on June 1, 2027. | Civil Works |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Assumption - A24 - Our schedule assumes the Wilbarger County Road Use Agreement (RUA) will be approved by Oct 1, 2025. | Civil Works |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Assumption - A25 - Our schedule assume improvements of the joint Solar/oil well Access Roads can begin as soon as the RUA is approved (i.e. since the roads are already in place, a driveway permit will not be required). | Civil Works |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Assumption - A26 - Assume there will be no interference with Wind Farm construction activities on the Access Roads included in the RUA. | Civil Works |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Assumption - A27 - Assume average module delivery rate of 30MW/week. | Civil Works |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Assumption - A28 - Assume tree clearing, chipping and spreading can start anytime. Assumes the SWPPP needs to be inplace prior to stump removal. | Civil Works |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Clarification - C1 - An additional corrosion study will be provided by JDH corrosion, based on the corrosion potential in the geotech report. | Contractor General |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Clarification - C2 - Primoris is requesting 0.4% of total modules for construction spares. | Contractor General |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Clarification - C3 - Performance testing: Primoris agrees to an ASTM standard-based Capacity Test, which is the industry standard performance guarantee in the US. This is the same approach taken on Bellefield II. All performance testing shall be executed at the plant level, not at the circuit level. | Contractor General |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Clarification - C4 - Contractor guarantees that the Capacity Test output will be equal to or greater than 97% of the Expected Capacity in accordance with certain criteria as will be more precisely detailed in an exhibit to the EPC Contract (the “Guaranteed Capacity”), the terms of which shall be subject to negotiation by the parties prior to the execution of the EPC Contract. | Contractor General |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Clarification - C5 - Construction spares have been included for the PV plant construction. | Contractor General |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Clarification - C6 - Pricing for MET equipment includes design engineering, procurement, installation, and commissioning of the following equipment: 13 Zenith MET Stations: -1 GHI Pyranometer, 1 POA Pyranometer, 3 RPOA Pyranometers, 1 All-in-one Weather Sensor, 1 Rain Gauge, 1 Lightning Rod*, 4 Surge Arrestors* (1 per array pyranometer) 13 Eclipse Soiling Stations 5 Standalone Albedometers: -1 GHI Pyranometer, 1 RGHI Pyranometer *Lightning rod and surge arrestors added at recommendation of MET vendor due to the project being located in an area of elevated lightning risk. | Detailed Design & Construction Engineering - 30% to IFC |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Clarification - C7 - SCADA proposal includes the latest exhibits for Crescent PV, which is different from BF2. Based on ask from AES to make suggestions for improvements we have come up with some items and possible approximate cost savings: -Canary Historian ~$500K -Cisco Firewalls ~ $20K -1GB Field Network ~ $200K | Detailed Design & Construction Engineering - 30% to IFC |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Clarification - C8 - 750 kcmil cable length mentioned in the client's 30% design is 164,678 LNFT less than PRE's calculated value( three phase). Our analysis is that the client has not considered, the parallel run lengths in the calculation. | Detailed Design & Construction Engineering - 30% to IFC |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Clarification - C9 - Base bid proposal pricing (based on 30%) includes cost for 1,080 silt fence rock outlets although the Westwood 30% drawings do not show these. Primoris assumed silt fence rock outlets would be used at intervals of 250 feet along silt fence. | Civil Works |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Clarification - C10 - Base bid proposal pricing (based on 30%) does not include cost for fiber roll, rock check dams, or diversion swales since the Westwood 30% drawings do not show these. | Civil Works |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Clarification - C11 - Proposal pricing include cost for third party SWPPP inspections. | Civil Works |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Clarification - C12 - The tracker design is using 60 degree stow which differs from the 30% Westwood design 75 degree. | Civil Works |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Clarification - C13 - Pre-drill PLT's was not performed by ANS and pre-drill with an undersize hole will be required to confirm the driven pile design parameters. | Civil Works |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Clarification - C14 - Additional PLT drivability testing will be required to confirm areas of pre-drill for driven pile install. | Civil Works |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Clarification - C15 - We have included installation and maintenance of the Switchyard/Substation Access Road in our scope. Depending on the construction schedule for the switchyard, the road may be built before our schedule dictates (Mar'26). | Civil Works |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Clarification - C16 - An alternate price for procurement, installation and commissioning of 153 SMA model SC4400 UP-US Inverters is offered. To meet the project schedule an accelerated Commissioning Schedule (50 calendar day duration) and a supply of commissioning spares is recommended. | Civil Works |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Clarification - C17 - The SMA Inverters offered here include a 55 degree C ambient temperature option. | Civil Works |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Clarification - C18 - Per the exhibit D-8 and D-8.1, Primoris will provide a dedicate on-site staff to develop the social management plan, community engagement meetings, create risk mitigation (includes noise, dust, signage), job fair planning and participation, weekly/ monthly compliance updates, and owner-led social impact session. The cost associated with this will be provided as below the line allowance. | Civil Works |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Clarification - C19 - The project schedule dictates we start construction work on the East side of the project and the west side at the same time. Consequently we will not be following the SWPPP staging plan described in the 30 design, drawing PV-C.01.05r1. | Civil Works |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Clarification - C20 - Pricing for basins aligns with Westwood's 30% drawings which indicate all basins will be temporary converted to permanent. Price may change for basin reclamation if basins are to be temporary only. | Civil Works |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Clarification - C21 - Base price includes 90% pre-drill. Adder for 100% pre-drill will be provided below the line. | Civil Works |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Clarification - C22 - Removal and disposal of existing and/or non-project generated refuse or debris beyond what's described in the 30% design. | Civil Works |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Exclusion - E1 - Hail protection of the PV modules when in the pallet or installed on the tracker (60 degree HailPro). | Contractor General |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Exclusion - E2 - Monies for discovery and/or removal of underground tanks, flow lines, pipes, and foundations. | Contractor General |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Exclusion - E3 - No double handling of modules is included. | Contractor General |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Exclusion - E4 - Module washing during or after installation. | Contractor General |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Exclusion - E5 - Scanning of each barcode on every module installed. | Contractor General |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Exclusion - E6 - Lightning protection for PV Inverters. | Contractor General |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Exclusion - E7 - Per the exhibit P, no O&M spares are included. The Parties shall enter into a Change Order to amend the Contract Price to include such elected Spare Parts post Notice to Proceed. | Contractor General |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Exclusion - E8 - Back of module temperature sensors, as AES has informed PRE that neither the ISO or forthcoming PPAs shall require them. | Plant Controls and Communications |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Exclusion - E9 - Removal or remediation of any contaminated soils or hazardous materials encountered. | Civil Works |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Exclusion - E10 - Primoris has excluded any rock trenching, rock blasting, mechanical breaking or rock drilling. | Civil Works |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Exclusion - E11 - Temporary or permanent relocation of existing utilities beyond what's described in the 30% design. | Civil Works |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Exclusion - E12 - Not responsible for crop damage, livestock protection or drain tile repair/mitigation. | Civil Works |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Exclusion - E13 - Removal of underground tanks, flow lines, pipes, and foundations. | Civil Works |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Exclusion - E14 - Material trucking between each half of the project or material export off site. | Civil Works |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Assumption - A1 - Proposal includes the provision of a 20 MVAR capacitor bank per MPT. PPS reserves the right to adjust the pricing based on the findings of the reactive power study. | HV |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Assumption - A2 - Proposal assumes the main power transformer setting, filling, and testing will be done by manufacturer and assumed duration of two weeks. | HV |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Clarification - C1 - This proposal is based on non-union labor. | HV |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Clarification - C2 - Proposal validity is 30 days. | HV |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Clarification - C3 - Proposal includes a two year workmanship warranty for the substation. | HV |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Clarification - C4 - HV demarcation is at the dead end structure of the substation. | HV |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Clarification - C5 - Substation work schedule is based on continuous work at six days a week (Monday through Saturday) at 10 hours per day. | HV |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Clarification - C6 - PPS will provide substation on-site orientation and familiarization (O&F) to owner and operator to introduce the system and its key components before the expected O&M handoff date. Formal training on system operation and preventative or corrective maintenance is the responsibility of the owner and operator. | HV |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Clarification - C7 - Storage for the owner provided HV circuit breakers is included. | HV |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Exclusion - E1 - Primoris will not cover any cost for the storage of the main power transformers. | HV |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Exclusion - E2 - The main power transformer setting, filling, and testing. | HV |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Exclusion - E3 - Post harmonic testing. | HV |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Exclusion - E4 - Substation rock excavation. | HV |  |  | 0 | Duplicate (stated in both SOV and proposal letter)
Assumption - A17 - All dirt work is full machine excavation. | Civil Works | No |  | 0
Assumption - A18 - Assume all powerlines, roads, and easements can be bored under. | Civil Works | No |  | 0
Assumption - A2 - PPS assumes all circuit crossings will be done with outages, and will be de-energized. | AC Electrical Systems | No |  | 0
Assumption - A3 - We have assumed a total of 330,500lbs for the steel poles. | AC Electrical Systems | No |  | 0
Assumption - A4 - We have assumed a total of 1,015CY of concrete for the drilled piers. | AC Electrical Systems | No |  | 0

## Project Team
Team Members | Name
SCADA Engineer | Mark Oliver
Real Estate | Josh Phillips
Permitting | Megan Lisburg
Legal | Trent Raleigh
Interconnection | Cory Blair
HV Engineer | Tyler Hock
Execution PM | Jon Coyne
Execution Engineer | Naveena Kodakandla
Estimator | Brent Anderson
Development Engineer | Sam Desai
Developer | Page Bolin
Contract Manager | Daniela Rojas

## Scope Categories
Procurement
30% Design Package
Detailed Design & Construction Engineering - 30% to IFC
Contractor General
Civil Works
Solar PV Field Mechanical
DC Electrical Systems
AC Electrical Systems
Plant Controls and Communications
Contractor Testing & Commissioning
HV

## 8.08.2025 Changes
PV Assumptions — Differences
Tariff cutoff date
7/28: “through mid-July, 2025” (below-the-line).
8/08: “through end of July 2025” (below-the-line).
Pile embedment & basis of loads
7/28: Max embedment 9'; based on “Nextracker’s HailPro 60° stow” loads.
8/08: Max embedment 8'; based on “Nextracker’s HailPro 60° stow” loads.
Power factor for losses
7/28: 0.94.
8/08: 0.92.
Ampacity basis
7/28: “Ampacity values provided by the client's Ampacity report.”
8/08: Uses thermal resistivity values from client geotech for ampacity calculations.
MV cable concentric neutral sizing note
7/28: Lists CN sizes and states “These sizes are bigger than the size mentioned in the client's 30% design.”
8/08: Lists the same CN sizes but drops the “bigger than 30% design” remark.
New MV design/installation assumptions added in 8/08 (no 7/28 counterparts):
Trefoil configuration used for MV ampacity.
Spiderplow installation method for MV cable.
90% compaction from thermal resistivity report; plowing most efficient.
SMA 4400 (55 °C option) values used to calculate number of skids.
Water sourcing / volume
7/28: Assumes on-site wells; requires ~100 million gallons; $0.50/barrel (37 gal).
8/08: Same sourcing & price; requires ~80 million gallons.
Access roads / schedule assumptions (selected)
Module delivery rate
7/28: 30 MW/week.
8/08: 18 MW/week.
Basins
7/28 (Clarification C20): Pricing aligned to temporary converted to permanent; price may change if temporary only.
8/08 (Assumption A33): Assumes all basins will be temporary; price may change if permanent required.
PV Clarifications — Differences
MET / soiling / albedo instrumentation counts
7/28 (C6): 13 Zenith MET, 13 Eclipse soiling, 5 standalone albedometers.
8/08 (C6): 10 Zenith MET, 10 Eclipse soiling, 3 standalone albedometers.
SCADA “suggested removals” cost-savings magnitudes
7/28 (C7): Canary Historian ~$500k; Cisco Firewalls ~$20k; 1 GB Field Network ~$200k.
8/08 (C7): Canary Historian ~$400k; Cisco Firewalls ~$20k; 1 GB Field Network ~$150k.
Cable length discrepancy note (750 kcmil)
7/28 (C8): Notes 164,678 LNFT delta vs. client’s 30% design and cause.
8/08: This note is not present in the August clarifications section provided. (No counterpart under C1–C19.)
Erosion/sediment controls
7/28 (C9–C10): Adds 1,080 silt fence rock outlets assumption and excludes fiber roll, rock check dams, diversion swales (not shown on 30%).
8/08: These two lines do not appear; Clarifications now begin with SWPPP inspections (C9).
SWPPP inspections
7/28 (C11): Included.
8/08 (C9): Included (renumbered and restated).
Tracker stow angle
7/28 (C12): 60° stow vs. Westwood 75°.
8/08 (C10): 60° stow “per guidance from AES.”
Pre-drill PLTs & drivability
7/28 (C13–C14): Pre-drill PLTs not performed by ANS; additional PLT drivability testing required.
8/08 (C11–C12): Same requirements, renumbered.
Switchyard/Substation access road
7/28 (C15): Included; may precede schedule (Mar ’26).
8/08 (C13): Same language.
Alternative SMA inverter procurement line item
7/28 (C16): Alternate for 153 SMA SC4400 UP-US; 50-day accelerated commissioning.
8/08 (C14): Alternate for 116 SMA SC4400 UP-US; 40-day accelerated commissioning.
55 °C inverter option (statement location)
7/28 (C17): 55 °C option included.
8/08 (C15): Same statement, renumbered.
Social management plan
7/28 (C18): Provided as below-the-line allowance.
8/08 (C16): Same content (renumbered).
Concurrent east/west start (SWPPP staging deviation)
7/28 (C19): Start East & West simultaneously; won’t follow SWPPP staging in 30% plan.
8/08 (C17): Same content (renumbered).
Pre-drill percentage (base price)
7/28 (C21): 90% included; adder for 100%.
8/08 (C18): 93% included; adder for 100%.
Debris removal beyond 30% design
7/28 (C22): Listed.
8/08 (C19): Listed (renumbered).
Tracker stringing approach (new in 8/08)
8/08 (C8): Switch to 4-string trackers; counts: 8,403 (4-string), 232 (3-string), 1,520 (2-string). (No 7/28 counterpart.)
PV Exclusions — Differences
Module washing “below-the-line” option explicitly added
7/28 (E4): Excludes module washing during/after install.
8/08 (E8): Restates exclusion and adds below-the-line one-time mobilization & wash option TBD.
Back-of-module temperature sensors wording
7/28 (E8): Excluded; references PRE.
8/08 (E9): Same exclusion; refers to Primoris (editorial name change).
Civil/environmental exclusion list renumbered in 8/08 (content same, numbering E10–E15).
Substation — Differences
Entity name in assumptions/clarifications
7/28 uses PPS in some substation items.
8/08 uses Primoris; otherwise content matches for A1–A2 and C1–C7.
Substation exclusions: Language materially unchanged (storage/testing exclusions; rock excavation exclusion).
MV Overhead — Differences
Entity naming
7/28: Assumptions & exclusions reference PPS (ROW laydown, outage crossings, pole/concrete quantities; no rock drilling).
8/08: Same technical content appears under Primoris (wording alignment), no substantive changes noted.
Summary of the most material shifts
Design/Calc Inputs: PF 0.94 → 0.92; embedment 9' → 8'; ampacity basis moved to geotech thermal; added trefoil and spiderplow assumptions; SMA 55 °C explicitly used for skid counts.
Quantities/Logistics: MET/soiling/albedo stations 13/13/5 → 10/10/3; module delivery 30 → 18 MW/week; pre-drill in base 90% → 93%.
Water: ~100M gal → ~80M gal (price unchanged).
Basins: From “temp → permanent per 30% (price may change if temp only)” to “all temporary (price may change if permanent).”
SCADA VE: Suggested removal cost deltas reduced ($500k → $400k, $200k → $150k).
Alt inverter option: 153 units / 50-day (7/28) → 116 units / 40-day (8/08).
Exclusions (clarity): Module washing exclusion now adds a defined below-the-line option (8/08).

## Sheet1
ACE Item | Change (8/08 vs 7/28)
1. Assume average module delivery rate of 30MW/week. | Changed: 18 MW/week in 8/08 (was 30).
2. Primoris is requesting 0.4% of total modules for construction spares.
1. SMA 4400 (153 units) to be supplied by AES.
2. An alternate price for procurement, installation and commissiong of 153 SMA model SC4400 UP-US Inverters is offerred. To meet the project schedule an accelerated Commissioning Schedule (50 calendar day duration) and a supply of commissionng spares is recommended. | Changed: alternate now 116 SMA SC4400 UP-US with 40-day accelerated commissioning (was 153 units, 50 days).
3. The SMA Inverters offerred here include a 55 degree C ambient temperature option.
The tracker design is using 60 degree stow which differs from the 30% Westwood design 75 degree. Domestic Content: 19.3 pts
1. Piles are assumed to be non coated (black steel) ranging from W6X12 up to W6X25, with tracker pile reveal height ranging from 5.25’ to 6’, with a max embedment depth of 9’. | Changed: max embedment 8’ in 8/08 (was 9’); loads basis updated to Nextracker “FT HailPro” 60° stow.
2. Uncoated “black steel” foundation design will be included in the proposal.
1. Pre-drill PLT's was not performed by ANS and pre-drill with an undersize hole will be required to confirm the driven pile design parameters.
2. Additional PLT drivability testing will be required to confirm areas of pre-drill for driven pile install.
3. Includes additional PLTs and supplemental Geotech studies.
4. An additional corrosion study will be provided by JDH corrosion, based on the corrosion potential in the geotech report.
1. Price includes Engineering services for Electrical, Civil, and Structural through IFC.
2. Max design temperature at the site used is 42.1C according to ASHRAE.
3. SCAN station used to obtain soil temperature and moisture value - 2202 Vernon
1. Construction spares have been included for the PV plant construction.
2. Per the exhibit P, no O&M spares are included. The Parties shall enter into a Change Order to amend the Contract Price to include such elected Spare Parts post Notice to Proceed.
3. Per the exhibit D-8 and D-8.1, Primoris will provide a dedicate on-site staff to develop the social management plan, community engagement meetings, create risk mitigation (includes noise, dust, signage), job fair planning and participation, weekly/ monthly compliance updates, and owner-led social impact session. The cost associated with this will be provided as below the line allowance.
Bid has been prepared based on PRE’s experience in Texas and assumes the following: (1) any executed contract will be considered separated for Texas sales/use tax purposes and (2) AES will provide an executed Texas exemption certificate, Form 01-339. Sales tax has been included on all items consumed/used by the contractor, i.e. construction equipment, consumables, etc. Additionally, bid includes estimated sales tax due on tracker and piles. PRE will coordinate with AES to confirm any exemptions to be claimed, ensure Schedule of Values is separated for Texas sales/use tax purposes, and calculate estimated taxes due. Changes to SOV format and/or exemptions to be claimed may result in a change in Contract Price.
1. Assume there are no un-surveyed underground lines not included in the client-provided surveys.
2. The Crescent Archeological Study ("8.Crescent-Historical-_Archaeological_Study-Final_04-22-2023.pdf") identifies two potential historical structures within the project area. However, it is unknown if the structures are extant and an aerial imagery search does not identify any visible structures. Therefore, Primoris has assumed these structures are no longer extant and do not require avoidance.
3. Assume the project lies outside of the tricolored bat range and that there are no tree clearing restrictions due to bats.
4. Assume tree clearing, chipping and spreading can start anytime. Assume the SWPPP need to be inplace prior to stump removal.
Texas Kangaroo Rat is not expected to occur in the project area. Primoris assumes no survey, mitigation and/or avoidance is required for this species.
1. Primoris has included 520,000 cubic yards of cut and 520,000 cubic yards of fill has been carried per the table on PV-C.02.01. Primoris has assumed that all material will be cut to fill on site and each parcel will be balanced.
2. Assume all soil spoils will be spread on-site.
3. The proposal does not include any allowance for rock, slurry, or cased/shored excavation. We are assuming dry, stable earth excavation for completion of all excavation activities pending being provided a geotechnical report.
4. All dirt work is full machine excavation.
5. Pricing for basins aligns with Westwood's 30% drawings which indicate all basins will be temporary converted to permanent. Price may change for basin reclamation if basins are to be temporary only. | Changed: 8/08 assumes all basins will be temporary; price may change if permanent basins are required.
1. Base bid proposal pricing (based on 30%) includes cost for 1,080 silt fence rock outlets although the Westwood 30% drawings do not show these. Primoris assumed silt fence rock outlets would be used at intervals of 250 feet along silt fence. | Removed in 8/08: not present.
2. Base bid proposal pricing (based on 30%) does not include cost for fiber roll, rock check dams, or diversion swales since the Westwood 30% drawings do not show these. | Removed in 8/08: not present.
3. Proposal pricing include cost for third party SWPPP inspections.
4. The project schedule dictates we start construction work on the East side of the project and the west side at the same time. Consequently we will not be following the SWPPP staging plan described in the 30 design, drawing PV-C.01.05r1.
1. Our schedule assume immprove of the joint Solar/oil well Access Roads can begin as soon as the RUA is approved (i.e. since the roads are already in place, a driveway permit will not be required)
2. We have included installation and maintenance of the Switchyard/Substation Access Road in our scope. Depending on the construction schedule for the switchyard,the road may be built before our schedule dictates (Mar'26)
1. FM1763, CR 105S, and FM 2897S Roads are suitable for construction traffic and may be used for site access.Refer to the provided draft "Site Access Routes" for full breakdown of assumed legths and maintanance plan. Price to be finalized with RUMA final approval. Primoris has also assumed there will be no other construction traffic on these roads during our construction schedule.
2. Our schedule assumes the Wilbarger County Road Use Agreement (RUA) will be approved by Oct 1, 2025.
3. Assume there will be no interference with Wind construction activites on the Access Roads included in the RUA.
Not responsible for crop damage, livestock protection or drain tile repair/mitigation.
Includes 6' chain link fence with 1' 3 barbed wires and gates.
1. Removal and disposal of existing and/or non-project generated refuse or debris beyond what's described in the 30% design.
2. Provisions for discovery and/or removal of underground tanks, flow lines, pipes, and foundations are not included.
3. Excludes temporary or permanent relocation of existing utilities beyond what's described in the 30% design.
4. Excludes removal of underground tanks, flow lines, pipes, and foundations.
Includes O&M building for 725MWdc size project per the O&M Specs 'O&M_Portable_Facility_Parameters' provided by AES.
Base price includes 90% pre-drill. Adder for 100% pre-drill will be provded below the line. | Changed: base includes 93% pre-drill in 8/08 (adder for 100% remains).
Tracker row lengths are based on module dimensions from the provided module data sheet Hi-Mo 545W (2278 x 1134 x 30 mm).
"1. Modules considered are LR5-78HBD-545M (Hi-Mo 545W). Modules will be procured and delivered to site by Owner. Primoris will be responsible for
offloading, Staging, and Installation of modules."
2. Price excludes Hail protection of the PV modules when in the pallet or installed on the tracker (60 degree HailPro).
3. Price excludes module washing during or after installation. | Changed: 8/08 adds a below-the-line one-time mobilization & wash option (TBD).
4. Scanning of each barcode on every module installed is excluded.
5. Double handling of modules is not included.
"Price includes Shoals DC Collection System.
Installation of PV string wiring is included in 'Furnish & Install PV Wire Harnessing & Combiner Box Disconnects' bid item."
Includes purchase & install of Harness, Trunk Bus, LBDs, Splice Boxes.
Includes purchase and imstall of cable management system.
Native soil will be suitable for backfilling trenches. No costs have been included for imported or engineered backfill.
"Price includes rough-in, grounding, and inverter installation.
Lightning protection for PV Inverters is excluded."
1. Power factor of 0.94 assumed for losses calculations | Changed: PF 0.92 assumed in 8/08.
2. Ampacity values provided by the client's Ampacity report was used. | Changed: ampacity based on geotech thermal resistivity; trefoil configuration; spiderplow installation; 90% compaction.
3. MV Rev C cables with concentric neutral size 18#14 AWG is assumed for 500kcmil, 750kcmil and 1000kcmil cables and CN size of 17#14 AWG for 4/0 cables. These sizes are bigger than the size mentioned in the client's 30% design. | Editorial: same CN sizes in 8/08; “bigger than 30% design” remark removed.
4. Ground cable size assumed in the design is 7#7AWG which is equivalent to the client mentioned 1/0 Cu.
5. MVAC cable collection loss % assumed is 0.85.
6. Assume all powerlines, roads, and easements can be bored under.
7. 750 kcmil cable length mentioned in the client's 30% design is 164,678 LNFT less than PRE's calculated value( three phase). Our analysis is that the client has not considered, the parallel run lengths in the calculation. | Removed in 8/08: this discrepancy note does not appear.
1. Pricing is based on client provided 30% design drawings.
2. Assumed MVOH losses=0 for calculations.
3. 30% MV OH design does not include part numbers or material quantities so estimated quantities were used to determine pricing.
4. We have assumed a total of 330,500lbs for the steel poles.
5. We have assumed a total of 1,015CY of concrete for the drilled piers.
"1. Pricing for MET equipment includes design engineering, procurement, installation, and commissioning of the following equipment:
13 Zenith MET Stations:
-1 GHI Pyranometer, 1 POA Pyranometer, 3 RPOA Pyranometers, 1 All-in-one Weather Sensor, 1 Rain Gauge, 1 Lightning Rod*, 4 Surge Arrestors* (1 per array pyranometer)
13 Eclipse Soiling Stations
5 Standalone Albedometers:
-1 GHI Pyranometer, 1 RGHI Pyranometer
Changed: counts reduced in 8/08 to 10 Zenith MET, 10 Eclipse soiling, 3 standalone albedometers.
*Lightning rod and surge arrestors added at recommendation of MET vendor due to the project being located in an area of elevated lightning risk."
"2. SCADA proposal includes the latest exhibits for Crescent PV, which is different from BF2.
Based on ask from AES to make suggestions for improvements we have come up with some items and possible approximate cost savings:
-Canary Historian ~$500K
-Cisco Firewalls ~ $20K
-1GB Field Network ~ $200K." | Changed: 8/08 VE deltas reduced — Canary Historian ≈$400k and 1 GB Field Network ≈$150k (Cisco Firewalls ≈$20k unchanged).
3. Back of module temperature sensors, as AES has informed PRE that neither the ISO or forthcoming PPAs shall require them.
1. Performance testing: Primoris agrees to an ASTM standard-based Capacity Test, which is the industry standard performance guarantee in the US. This is the same approach taken on Bellefield II. All performance testing shall be executed at the plant level, not at the circuit level.
2. Contractor guarantees that the Capacity Test output will be equal to or greater than 97% of the Expected Capacity in accordance with certain criteria as will be more precisely detailed in an exhibit to the EPC Contract (the “Guaranteed Capacity”), the terms of which shall be subject to negotiation by the parties prior to the execution of the EPC Contract.
Assumption - A1 - Tariffs are not included in the base price SOV. The estimated tariffs through mid-July, 2025 have been presented below the line for each procurement category. | Changed: tariffs estimated through end of July 2025 (still below-the-line).
"Assumption - A2 - Bid has been prepared based on PRE’s experience in Texas and assumes the following: (1) any executed contract will be considered separated for Texas sales/use tax purposes and (2) AES will provide an executed Texas exemption certificate, Form 01-339. Sales tax has been included on all items consumed/used by the contractor, i.e. construction equipment, consumables, etc. Additionally, bid includes estimated sales tax due on tracker and piles. PRE will coordinate with AES to confirm any exemptions to be claimed, ensure Schedule of Values is separated for Texas sales/use tax purposes,
and calculate estimated taxes due. Changes to SOV format and/or exemptions to be claimed may result in a change in Contract Price."
"Assumption - A3 - Piles are assumed to be non coated (black steel) ranging from W6X12 up to W6X25, with tracker pile
reveal height ranging from 5.25’ to 6’, with a max embedment depth of 9’. The pile sizes are based on Nextracker's HailPro 60 degree stow top of pile loads." | Changed: embedment 8’ and loads basis updated to Nextracker “FT HailPro” 60° in 8/08.
Assumption - A4 - Power factor of 0.94 assumed for losses calculations. | Changed: 0.92 in 8/08.
Assumption - A5 - Ampacity values provided by the client's Ampacity report was used. | Changed: ampacity now based on geotech thermal resistivity; trefoil configuration; spiderplow installation; 90% compaction.
"Assumption - A6 - MV Rev C cables with concentric neutral size 18#14 AWG is assumed for 500kcmil, 750kcmil and
1000kcmil cables and CN size of 17#14 AWG for 4/0 cables. These sizes are bigger than the size mentioned in the client's 30% design." | Editorial: same CN sizes in 8/08; “bigger than 30% design” remark removed.
Assumption - A7 - Ground cable size assumed in the design is 7#7AWG which is equivalent to the client mentioned 1/0 Cu.
Assumption - A8 - Assumed T-line losses=0 for calculations.
Assumption - A9 - MVAC cable collection loss % assumed is 0.85.
Assumption - A10 - Max design temperature at the site used is 42.1C according to ASHRAE.
Assumption - A11 - SCAN station used to obtain soil temperature and moisture value - 2202 Vernon.
"Assumption - A12 - Primoris has assumed that the on-site water wells can be used for the dust mitigation purpose. Throughout the project duration, Primoris would require ~100 million gallons of water for backfill and dust control. Proposal assumes that the water can be purchased through the landowner at $0.50 per barrel of water. One barrel of water shall be defined as 37 gallons. We have assumed that there is at least one | Changed: ~80 million gallons in 8/08 (price and 37-gal barrel definition unchanged).
well in East and one in West parcel within the project boundary and each well produces ~100k gallons per day."
"Assumption - A13 - FM1763, CR 105S, and FM 2897S Roads are suitable for construction traffic and may be used for site access. Refer to the provided draft ""Site Access Routes"" for full breakdown of assumed lengths and maintenance plan. Price to be finalized with RUMA final approval. Primoris has also assumed there will
be no other construction traffic on these roads during our construction schedule."
Assumption - A14 - Native soil will be suitable for backfilling trenches. No costs have been included for imported or engineered backfill.
Assumption - A15 - All soil spoils will be spread on-site.
"Assumption - A16 - The proposal does not include any allowance for rock, slurry, or cased/shored excavation. We are assuming dry, stable earth excavation for completion of all excavation activities pending being provided a
geotechnical report."
Assumption - A17 - All dirt work is full machine excavation.
Assumption - A18 - Assume all powerlines, roads, and easements can be bored under.
Assumption - A1 - PPS assumes ROW can be used as laydown area. | Editorial: naming aligned to “Primoris” in 8/08; technical content unchanged.
Assumption - A2 - PPS assumes all circuit crossings will be done with outages, and will be de-energized. | Editorial: naming aligned to “Primoris” in 8/08; content unchanged.
Assumption - A3 - We have assumed a total of 330,500lbs for the steel poles.
Assumption - A4 - We have assumed a total of 1,015CY of concrete for the drilled piers.
Exclusion - E1 - PPS has not included any rock drilling in this proposal.